## Project Delivery
Project Delivery Brief
Servicing and Repair of M & E Installations – Fire- within properties owned/managed by Aster Group
Preamble
All materials and workmanship are to achieve the Aster expectation to remain compliant at all times and unless otherwise stated/permitted, materials are to be new. All works are to be carried out in strict accordance with the instructions given by the Contract Administrator from time to time during the progress of the works and to their entire satisfaction.
All goods, materials and workmanship used in the Works shall, so far as is practicable and unless otherwise specified, have been produced in the United Kingdom or any other EEC member country. No deviation from specified materials will take place without written authority.
Where a Standard or Code of Practice issued by the British Standards Institution or a European equivalent, the date at tender is appropriate, goods, materials and workmanship used in the Works, unless otherwise described, shall be in accordance with that standard.
The letters “BS” followed by a number refers to particular British Standards published by the British Standards Institution. The relevant items must comply with the quoted BS, together with all amendments current at the date of tender.
In addition to the compliance with the provisions of the British Standards and Codes of Practice, the works shall comply with all relevant statutory instruments and regulations current at the date of tender (unless stated otherwise in this Specification) and in particular, with the following:
Working at Height Regulations 2005 and amendments
Control of Asbestos Regulations 2012
Health and Safety at Work Act 1974
Control of Substances Hazardous to Health Regulations 2002
Construction (Design and Management) Regulations 2015
ECA Wiring Regulations
Regulatory Reform (Fire Safety) Order 2005
Building Regulations
It is the aim of this agreement that the bodies involved will aim to
Undertake the servicing and repair of the fire protection provision at the properties listed. This will include but is not limited to
Servicing and maintenance of fire Alarms;
servicing and maintenance of fire fighting equipment
servicing and maintenance of sprinkler systems
servicing and maintenance of dry risers
Servicing and maintenance of Automatic smoke vents
Servicing and Maintenance of door closers and interlinks
Servicing and maintenance of door hold open devices
Provide an out of hours emergency service
Provision of a responsive repairs service for the above elements
Create a mutually beneficial partnership Involving Aster, Contractor and any suppliers and third parties to bring about successful projects from inception through to completion
To develop and evolve a maintenance schedule and replacement program.
Call outs and emergency attendance will all be within 2 hours.
Work in an open and honest way with shared information on products, budgets, programmes, specifications and costs.
Gain an understanding of the drivers behind the respective businesses to enable each partner to minimise the risks to each other by focusing on mutual interests.
Deliver this project and services in an environment of continuous improvement and achieving maximum value for each project and delivered safely, on time and to cost.
Location
This will form 1 of 3 lots. This lot is for Aster Properties located within the county of Cornwall.
Scope of Works
This work is to service and maintain the fire safety equipment at properties within the Aster Group.
Requirements
The successful contractor will work through the asset list to undertake the periodic servicing and reporting on each property. Any recommendation on the system or property are to be reported back in writing. No obligation to offer follow on work is provided. The CA will decide on the scale/scope and complexity of the works. Some items may be placed directly with the service contractor at the discretion of the CA. Any properties which the contractor believes are under specified or over specified for the provision of fire safety are to be raised with the CA
Program period
Servicing works will be undertaken throughout the year to meet the Association compliance requirement. Repair works and call outs will be undertaken in line with the draw off document and priorities set out in this document
Roles and responsibilities
Surveyor - Aster (will also be the named service manager within the NEC contract)
Role
1. To carry out day to date supervision of the works programme
2. To provide a first point of contact for tenants and to provide information and resolve queries as necessary
3. To undertake property surveys and provide the contractor with information to allow contract progression
4. Manage and Maintain Financial control including the undertaking of Valuations, variations, invoicing and production/review of certificates
5. Carry out quality control on servicing contract and monitor compliance.
6. Undertake monthly progress meetings producing minutes, and ensuring actions are completed and undertaken in a timely fashion
7. Carry out the contract administration in line with the Planned Maintenance Procedures
Responsibility
1. Ensure tenant consultation is carried out and act as first point of contact for all tenant contract queries
2. In conjunction with the Contractors Supervisor provide day to day management of the planned programme
3. Carry out on site inspections and liaise with tenants as required
4. Make on site decisions regarding the day to day delivery of the planned programme
5. Implement, on a day to day operational basis the working practices, procedures and policies set out in the Aster documentation
6. Report back to management any operational matters that require a change in working practice, procedure or policy
Servicing Manager- Aster
Role
1. Co-ordinate the different planned maintenance programmes on a day to day operational basis to ensure sufficient resources are in place
2. Provide day to day support to front line operational staff
3. To provide, in conjunction with the Operations Manager and head of Planned Maintenance, agreed performance data
Responsibility
1. Ensure that detailed programmes are developed, maintained and updated and report back to the planned maintenance monitoring group on progress against programme
2. Ensure that adequate staffing resources are available on the client side for each planned programme
3. Ensure information from each planned programme is cross referenced to other programmes to ensure no programme operates in isolation
4. Ensure appropriate administrative support is provided to the planned maintenance monitoring group to enable it to function efficiently and effectively
5. Ensure that key performance data is provided to the planned maintenance monitoring group Monthly
Technical Services Assistant Director - Aster (possibility some of role undertaken by others)
Role
1. To oversee the delivery of the works within Aster
2. Ensure team members remain focussed, committed and working in a constructive, co-operative way
3. Co-ordinate key performance data and ensure it is presented to any planned maintenance monitoring group meeting
4. To challenge and question current practice and procedure to ensure continuous improvement is achieved
5. To ask why and how
Responsibility
1. Ensure appropriate key performance information is provided to any planned maintenance monitoring group meeting
2. Provide support and direction to front line members of staff delivering the planned programmes in conjunction with the Planned Maintenance Manager
3. Monitor and manage expenditure to ensure financial arrangements are operating within target prices and report back to the planned maintenance monitoring group where this is not the case
4. To raise issues or concerns from an overall partnering approach to the planned maintenance monitoring group
5. Propose improvements and best practice examples to the planned maintenance monitoring group
6. To ensure the group is working effectively
7. To facilitate the development of new ideas and processes to improve effectiveness and efficiency of the arrangement
8. To ensure performance data is being collected and used
Site Manager/Supervisor- Contractor
Role
1. To carry out day to day supervision of the programme
2. To provide a first point of contact for tenants and to provide information and resolve queries as necessary
Responsibility
1. To co-ordinate the ordering and delivery of all materials required to carry out the planned programme
2. To supervise all operatives on a day to day basis and monitor individual performance
3. In conjunction with the Building Surveyor provide day to day management of the planned programme
4. Collect collate and provide Key performance information in line with the requirements of the planned maintenance monitoring group
5. Make on site decisions regarding the day to day delivery of the programme
6. Implement, on a day to day operational basis the working practices, procedures and policies agreed by the planned maintenance monitoring group
7. Report back to the planned maintenance monitoring group any operational matters that require a change in working practice, procedure or policy
8. To take day to day responsibility for health & safety and environmental issues
Contract Manager- Contractors
Role
1. To oversee the delivery of the contract within the contracting organisation
2. Ensure team members remain focussed, committed and working in a constructive, co-operative way
3. Co-ordinate key performance data and ensure it is presented to each planned maintenance monitoring group meeting
Responsibility
1. Ensure appropriate key performance information is provided to every planned maintenance monitoring group meeting
2. Provide day to day support and direction to front line members of staff delivering the planned programmes
3. Monitor and manage expenditure to ensure the financial arrangement is operating within target prices and report back to core group where this is not the case
4. To raise issues or concerns from an overall partnering approach to the planned maintenance monitoring group
5. To assist the Service Manager with reporting programme updates to the Planned Maintenance Monitoring group
6. To take overall responsibility for health & safety issues
Regional Director- Contractor
Role
1. To challenge and question current practice and procedure to ensure continuous improvement is achieved
2. To ask why and how
3. To develop the partnering approach within the contracting organisation
Responsibility
1. To lead on the development of the partnering arrangement
2. To ensure the group is working effectively
3. To facilitate the development of new ideas and processes to improve effectiveness and efficiency of the arrangement
4. To ensure performance data is being collected and used
Relationships, communications, detail and protocols –
Communication and conflict resolution
All information should start with the surveyor and site supervisor to resolve and or deal with. Escalation only takes place shoul the issue not be resolved within the stated time frame or conflict ensues over a decision/action
Aster |  |  | Contractor
Surveyor | çè | 5 days | Site Supervisor
Servicing Manager | çè | 5 days | Contracts Manager
Technical Service Assistant Director | çè | 10 days | Contractors Area Director
Timetables and programmes –
It is anticipated that this work will commence on site in April 2019. A program will be established jointly and used to monitor the servicing program
Pricing frameworks –
See document
Consultant service matrix –
At this stage no consultants will be party to this agreement
Combined risk register
A combined risk register will be produced with the successful contractor.
Material Supply and supply Chain relationship
Where appropriate the client reserves the right to introduce its own supply chain and/or services along with materials. Any pricing will be adjusted accordingly.
Providers appointed to the Contract may be required as main contractor within projects and to utilise supply chains already or yet to be established by Aster Property or the procurement clubs which support them.
Access for tender stage visits.
Several sites are access controlled. Any site visits to be arranged InTend requests. Any queries or questions are to be submitted through Intend. Any breach of this may result in tender exclusion.

## estimated values
lot | Previous esitimated value per annum
Cornwall | 7412
Devon | 24089
Dorset | 153799
185300
These are tendered as separate lots, but Aster reserve the right to award to a 1, 2 or 3 providers.

## Fire Alarms
Fire Alarms fully comprehensive Cover
Item | Rate per property any size, type of system location nr of panels or zones containing total nr of call points bells sounders smoke/heat detectors fire hydrants and door retainers | Cost |  |  |  | Nr of cornwall blocks/ Properties [e] | Total Approximate Cost Annual Cost ([a]+[b]+[c]+[d]) x [e]
|  | Planned inspections testing and Reporting |  |  | Fully comprehensive response Repairsand emergency call out facility [d]
|  | 3 months [a] | 6 months [b] | 12months [c]
1.01 | 1 to 50 | 0 | 0 | 0 | 0 | 5 | 0
1.02 | 51 to100 | 0 | 0 | 0 | 0 | 0 | 0
1.03 | 101 to150 | 0 | 0 | 0 | 0 | 1 | 0
1.04 | 151 to 200 | 0 | 0 | 0 | 0 | 0 | 0
1.05 | 201 to 250 | 0 | 0 | 0 | 0 | 0 | 0
1.06 | 251 to 300 | 0 | 0 | 0 | 0 | 0 | 0
1.07 | 301 to 350 | 0 | 0 | 0 | 0 | 0 | 0
1.08 | 351 to 400 | 0 | 0 | 0 | 0 | 0 | 0
Total cost per annum | [6 empty] | 0
**contractor to price all items 1.01 to 1.08 to allow for future development and expansion
Fire Alarms
On first visit all landlords provided equipment and services are to be clearly tagged with an asset number. This asset register shall be uploaded in an electronic format to the service manager.
Fire alarms shall be tested in accordance with the requirements of BS 5839-6 2013.
The inspection and testing should be carried out by a competent person.
If a risk assessment shows a need for more frequent inspection and servicing visits, then all interested parties should agree the appropriate inspection and servicing schedule. If this recommendation is not implemented, it should be considered that the system is no longer compliant with this part of BS5839
On completion of the work, the contractor should be satisfied that the systems operate correctly. Any outstnding defects should be be reported to the contract administrator, the system log book should be completed and a fire alarm Inspection and Servicing Certificate should be issued
3 Monthly Maintenance Visit
Electro Magnetic Door Catches and door closers
Test and adjust function of electromagnetic release device and door closer
Visually inspect wiring
Ensure electrical connections are clean and correct
Check door closers to ensure correct function, adjust as necessary
Rectify any defect and issue report to the contract administrator
Fire alarm systems
A visual inspection is to be made that the Fire risk assessment is still valid with the current building layout and that the fire alarm is fit for purpose.
All manual call points remain unobstructed and positioned in accordance with current standards
Ensure that detectors are able to function within their designated parameters
Ensure all batteries retain the required charge
The standby battery should be disconnected and followed by a full activation test.
The fire alarm functionality should be checked by the operation of at least one device on each circuit. Record on the log book which initiating device has been used for the test
The operation of 25% of the fire alarm devices should be checked
Check all panels for correct operation and indication
The operation of any facility for automatic transmission of alarm signals to an alarm receiving centre should be checked. Where more than one form of alarm signal can be transmitted (e.g. fire and fault signals), the correct transmission of each signal should be confirmed
All ancillary functions of the fire alarm system should be tested
Ensure self-diagnostic facilities function correctly
Radio systems of all types should be serviced in accordance with the recommendations of the manufacturer
Lead NiCad Batteries and Charger
Due to types of NiCad batteries varying, manufacturers instructions must be followed for the type of battery to be maintained. Maintenance tasks must be carried out in a well ventilated area
Check the serviceability of the battery and that the charger is compatible for the battery type. Should the charger be delivering the incorrect voltage then repair or replace as necessary
Ensure that the batteries are stored in a dust and damp free area
Check and ensure that battery terminations are secure, in good condition and appropriately greased
Apply a coating of Battery Terminal Grease or similar material to connectors and over the tops of cells
6 Monthly Maintenance Visit
All as per 3 monthly Maintenance Visits but with a check of 50% of the operation of the alarm devices in accordance with current regulations and manufacturers instructions
12 Monthly Maintenance Visit
Fire Alarm Systems
In addition to testing as for the three monthly maintenance Visits the following works should also be undertaken every year
100% test of all devices on the systems in accordance with the current regulations and manufacturers recommendations
Radio signal strengths in radio linked systems should be checked for adequacy
A visual inspection should be made to confirm that all readily accessible cable fixings are secured and undamaged
The cause and effect program should be confirmed as being correct
The standby power supply capacity should be checked to establish it remains suitable for continued service and replace if not
All further annual checks and tests recommended by the manufacturer of the control and indicating equipment and other components of the system should be carried out
Note: All testing products must be appropriate for purpose and the environment within which the systems are installed.
Test Certificates
All test certificates are to contain as a minimum
Relevant Aster UPRN
First line of address
Date of visit
System details
Clear indication of type of service
Time of Arrival and time of departure
Any Recommendations to be accompanied with fixed price quote
Any non emergency issues Identified to be picked up on scheduled next maintenance visit
Test results
Any defects rectified
Certificates
All works orders will be issued through Asters Contractor Portal. Training will be provided by Aster on its use. Orders will be issued though the portal, invoices submitted through the portal and all certificates necessitated for compliance and payment will be uploaded through the portal.

## Portable Fire Fighting Equipmen
Portable Fire Fighting Equipment- Fully Comprehensive Cover
Item | Rate per Unit containing any combination of the following portable fire fighting equipment including extinguishers, hose reels and fire blankets | Annual rate per unit for all inclusive responsive repairs | Annual rate per unit for planned works | Nr of Locations | Total cost per annum
2.01 | 1 to 10 units of any type of equipment and any single location | 0 | 0 | 1 | 0 | For clarity items 2.01 to 2.06 rate per unit x number of units at location will be the basis of any cost recovery by the contractor.
2.02 | 11 to 20 units of any type of equipment and any single location | 0 | 0 | 0 | 0
2.03 | 21 to 30 units of any type of equipment and any single location | 0 | 0 | 1 | 0
2.04 | 31 to 40 units of any type of equipment and any single location | 0 | 0 | 0 | 0
2.05 | 41 to 50 units of any type of equipment and any single location | 0 | 0 | 0 | 0
2.06 | 51 to 60 units of any type of equipment and any single location | 0 | 0 | 0 | 0
| Toatal cost per annum |  |  |  | 0
**contractor to price all items 2.01 to 2.06 to allow for future development and expansion
Fire Fighting Equipment
General Information
On first visit all landlords provided equipment and services are to be clearly tagged with an asset number. This asset register shall be uploaded in an electronic format to the service manager.
The requirement is for the execution of a fully comprehensive planned servicing, testing, maintenance and responsive repairs service. The cost to provide this service will be included within the rates/prices within this pricing document to create the annual sum. The cost of any replacement equipment will be reimbursed at the rate included in this pricing document
Fire Fighting Equipment includes but is not limited to the following
Fire extinguishers (wet Chemical, CO2, Water, Foam and dry powder
Hose Reels
Fire Blankets
Progress meetings will be held quarterly. The contract administrator will chair the meeting and issue any minutes
Scope of Works
The contractor shall include within their annual testing, servicing and maintenance sum and is responsible for
Large parts and components (hoses, Horns & H Caps)
All consumables (O-rings, clips, pins etc…)
All discharge tests & refills as per BS5306
Wall fixings (where missing)
I D signs (where Missing)
Certificates of testing
Number all pieces of equipment and draw up a maintenance record sheet showing known service history
Providing information and reports should malicious damage be identified or suspected
Excluded from the contractors annual testing, servicing and maintenance sum
CO2 Hydraulic test
New equipment
Vandalism, malicious or mischievous damage/use of equipment
Misused/discharged equipment
Refilling of extinguishers due to discharge in the event of a fire
If the contract Administrator requires a replacement item of equipment, not included within the contractors responsibilities above, this will be subject to a separate Works Order. The cost of the replacement shall be determined by the rates contained within this pricing document.
The contractor shall note the priority coding will be in the majority - Routine Repairs
The contractor shall complete and supply the information with in an asset schedule report. The completed asset schedule report along with the properties serviced in the quarter, including the next service due date shall be attached to the contractors invoice. The contractor shall note that payment may be delayed if the information required is not fully supplied at the time of the invoice.
Maintenance Procedure
All equipment shall be maintained in accordance with current legislation
12 Monthly Maintenance Visits
Hand Held fire fighting equipment
Ensure all equipment is located correctly to suit risk
Ensure all equipment is correctly wall mounted and secure
Examine extinguisher body for cylinder damage
Inspect service history to determine service procedure
Inspect medium if required
Remove, check weight & date of cartridge
On stored pressure units, weigh full extinguisher and test head gauge
CO2 units check weight and cylinder date and ensure horn safe
Inspect all discharge paths and ensure they are clear and head assembly is fully operational
Examine all pressure seals and threads and ensure that they are not damaged. Lubricate as required
Ensure that retaining pin and anti-tamper tags are intact
Record service details
Five yearly visit
Hand held fire fighting equipment
On the fifth year of the extinguishers last discharge test, the contractor shall include for and carry out in addition to the above, a full discharge test and refill
All chemical discharge waste to be removed from site and appropriately disposed of. Certification of disposal process is required
Asset Schedule Report
The contractor shall assign a reference to every item of portable equipment on their initial maintenance visit. This information shall be logged in an asset schedule as approved by the contract administrator
Certificates
All works orders will be issued through Asters Contractor Portal. Training will be provided by Aster on its use. Orders will be issued though the portal, invoices submitted through the portal and all certificates necessitated for compliance and payment will be uploaded through the portal.

## Sprinkler Systems
Sprinkler Systems
Item | Rate per element: planned testing, servicing, certification and maintenance | rate per system | Nr of systems | Total cost
3.01 | 6 monthly visit | 0 | 1 | 0
3.02 | 12 monthly visit | 0 | 1 | 0
Toatal cost per annum |  |  |  | 0
**contractor to price all items allow for future development and expansion
Sprinkler Systems
General Information
On first visit all landlords provided equipment and services are to be clearly tagged with an asset number. This asset register shall be uploaded in an electronic format to the service manager.
The requirement is the execution of planned service, safety inspection and maintenance to the associations sprinkler systems
The requirement is a comprehensive contract including the execution of planned inspections testing, remedial works and emergency call out facility. The cost to provide these services will be included within the rates/prices provided in the pricing document for the annual sum per site. The cost of replacement components will be reimbursable.
The contractor shall note the priority coding of callouts will be in the majority Emergency Repairs
Quarterly progress meetings will be held
Scope of Works
Excluded from the contractors fully comprehensive cover are
Any repairs caused by storm, vandalism, flood or wilful neglect by third parties
Maintenance Procedure
The contractor shall carry out the inspection and testing of the system and equipment as recommended in TB203 the care and maintenance of automatic sprinkler systems
Certificates
All works orders will be issued through Asters Contractor Portal. Training will be provided by Aster on its use. Orders will be issued though the portal, invoices submitted through the portal and all certificates necessitated for compliance and payment will be uploaded through the portal.

## Dry Riser
Dry Riser
Item | Rate per element: planned testing, servicing, certification and maintenance | rate per system | Nr of systems | Total cost
4.01 | 6 monthly visit | 0 | 0 | 0
4.02 | 12 monthly visit | 0 | 0 | 0
Toatal cost per annum |  |  |  | 0
**contractor to price all items to allow for future development and expansion
Dry Risers
General Information
On first visit all landlords provided equipment and services are to be clearly tagged with an asset number. This asset register shall be uploaded in an electronic format to the service manager.
The requirement is the execution of planned service, safety inspection and maintenance to dry Risers. The cost to provide this service will be included within the rates/prices contained within this document.
Progress meetings will be held quarterly
Scope of Work
The planned service, safety inspection and maintenance and repair will be undertaken by a competent person and to comply with the main requirements of BS9990:2015. The cost of replacement components will be at the rates and prices contained within the document.
Maintenance Procedure
6 Monthly Maintenance Visit
Inspection and if required repair of dry riser housing
Full visual inspection
Clear the riser of any debris
Check all exposed pipework and flanges
Check security of any anchor points and brackets
Check for integrity of fire stopping where pipes pass through walls or slab
Report Defects
Check condition of breaching connections and report
Check for full and free movement of all landing hydrant valves, checks hand wheel is secured correctly
Check all inlet and landing valves and associated washers are sound, replace as required
Check security of padlocks and tamper straps. Report back any issues
Check signage is correct and replace as necessary
12 Monthly Maintenance visit
Undertake a full test at pressure
Open the top valve of the system and flush out the system to remove any debris, ensuring no debris remains in the immediate vicinity
Test the system in accordance with current industry standards
Certificates
All works orders will be issued through Asters Contractor Portal. Training will be provided by Aster on its use. Orders will be issued though the portal, invoices submitted through the portal and all certificates necessitated for compliance and payment will be uploaded through the portal.

## Automatic smoke vents
Automatic smoke Vents
Item | Nr of ASV's at any single location to be serviced, maintained, certifcated and tested twice per year | rate per unit at location | Annual cost for fully comprehensive cover inclusive of remedial works, replacement components, responsive repairs and emergency call out facility for all of Dorset | Nr of locations | Total cost
5.01 | 1-5nr | 0 | 0 | 2 | 0 | For clarity items 5.01 to 5.05 rate per unit x number of systems will be the basis of any cost recovery by the contractor.
5.02 | 6-10nr | 0 | 0 | 0 | 0
5.03 | 11-15nr | 0 | 0 | 1 | 0
5.04 | 16-20nr | 0 | 0 | 0 | 0
5.05 | e/o each above 20 per location | 0 | 0 | 0 | 0
Toatal cost per annum |  |  |  |  | 0
**contractor to price all items 1.01 to 1.08 to allow for future development and expansion
Automatic Smoke Vents
General Information
On first visit all landlords provided equipment and services are to be clearly tagged with an asset number. This asset register shall be uploaded in an electronic format to the service manager.
The requirement is a fully comprehensive contract including the execution of planned inspections, testing, remedial works, and replacement components and emergency call out facility. The cost to provide these services will be included within the rates/prices provided in the pricing document for the annual sum
The contractor shall note the priority coding of call outs will be in the majority 'Emergency Repairs'
Scope of Works
Excluded from the contractors fully comprehensive cover are
Any repairs caused by storm, vandalism, flood or wilful neglect by third parties
Window glass and window frames unless the damage is caused by the contractor
Maintenance Procedure
The contractor shall carry out the inspection and testing of the systems and equipment as recommended in BS7346-8:2013 and BS558-5:2004. in particular the contractor must include for the following
6 monthly maintenance visits
Check and test that the smoke removal systems function correctly in fire conditions and close on resetting
Adjust and reset louvres, mechanisms and magnets as necessary to ensure smooth operation, leaving vent in fully working order
Repair and report any defects to contract administrator
Service all working parts
Record all results and service reports and issue to Contract Administrator within seven days of visit
Certificates
All works orders will be issued through Asters Contractor Portal. Training will be provided by Aster on its use. Orders will be issued though the portal, invoices submitted through the portal and all certificates necessitated for compliance and payment will be uploaded through the portal.

## Repairs
Spot Rates for repairs
Place a spot rate against each item for Dorset Properties
| Description | Cost | Unit
1 | Replace Fire Alarm smoke or heat detector (optical) | 0 | nr
2 | Replace fire alarm smoke or heat detector (ionisation) | 0 | nr
3 | Replace base for smoke or heat detector (optical) | 0 | nr
4 | Replace base for smoke or heat detector (ionisation) | 0 | nr
5 | Replace call point | 0 | nr
6 | Supply spare glasses for fire alarm call point | 0 | 5 nr
7 | Supply and fit spare glasses for fire alarm call point | 0 | nr
8 | Replace magnetic door retainer unit | 0 | nr
9 | Replace strobe light unit | 0 | nr
10 | Replace door closures | 0 | nr
11 | Replace sounder | 0 | nr
12 | Replace Battery Charger | 0 | nr
13 | Replace lamps for fire alarm panel | 0 | nr
14 | Replace batteries for fire alarm panels (any size) | 0 | item
15 | Supply site with fire test log book | 0 | nr
Fire Extinguishers
16 | Discharge test and refill | 0 | nr
17 | Refill of extinguisher | 0 | nr
18 | Replace water extinguisher | 0 | nr
19 | Replace foam extinguisher | 0 | nr
20 | Replace CO2 extinguisher | 0 | nr
21 | CO2 Hydraulic test | 0 | nr
22 | Replace dry powder extinguisher | 0 | nr
23 | Replace fire blanket | 0 | nr
24 | Replace horn and hose | 0 | nr
25 | supply |  | nr
26 |  |  | nr
27 |  |  | nr
28 |  |  | nr
29 |  |  | nr
30 |  |  | nr
31 |  |  | nr
32 |  |  | nr
33 |  |  | nr
34 |  |  | nr
35 |  |  | nr
36 |  |  | nr
37 |  |  | nr
38 |  |  | nr
39 |  |  | nr
40 |  |  | nr
41 |  |  | nr
42 |  |  | nr
43 |  |  | nr
44 |  |  | nr
45

## Maintenance Schedule
Maintenance Procedures-
On first visit all landlords provided equipment and services are to be clearly tagged with an asset number. This asset register shall be uploaded in an electronic format to the service manager.
Fire Alarms
Fire alarms shall be tested in accordance with the requirements of BS 5839-6 2013.
The inspection and testing should be carried out by a competent person.
If a risk assessment shows a need for more frequent inspection and servicing visits, then all interested parties should agree the appropriate inspection and servicing schedule. If this recommendation is not implemented, it should be considered that the system is no longer compliant with this part of BS5839
On completion of the work, the contractor should be satisfied that the systems operate correctly. Any outstnding defects should be be reported to the contract administrator, the system log book should be completed and a fire alarm Inspection and Servicing Certificate should be issued
3 Monthly Maintenance Visit
Electro Magnetic Door Catches and door closers
Test and adjust function of electromagnetic release device and door closer
Visually inspect wiring
Ensure electrical connections are clean and correct
Check door closers to ensure correct function, adjust as necessary
Rectify any defect and issue report to the contract administrator
Fire alarm systems
A visual inspection is to be made that the Fire risk assessment is still valid with the current building layout and that the fire alarm is fit for purpose.
All manual call points remain unobstructed and positioned in accordance with current standards
Ensure that detectors are able to function within their designated parameters
Ensure all batteries retain the required charge
The standby battery should be disconnected and followed by a full activation test.
The fire alarm functionality should be checked by the operation of at least one device on each circuit. Record on the log book which initiating device has been used for the test
The operation of 25% of the fire alarm devices should be checked
Check all panels for correct operation and indication
The operation of any facility for automatic transmission of alarm signals to an alarm receiving centre should be checked. Where more than one form of alarm signal can be transmitted (e.g. fire and fault signals), the correct transmission of each signal should be confirmed
All ancillary functions of the fire alarm system should be tested
Ensure self-diagnostic facilities function correctly
Radio systems of all types should be serviced in accordance with the recommendations of the manufacturer
Lead NiCad Batteries and Charger
Due to types of NiCad batteries varying, manufacturers instructions must be followed for the type of battery to be maintained. Maintenance tasks must be carried out in a well ventilated area
Check the serviceability of the battery and that the charger is compatible for the battery type. Should the charger be delivering the incorrect voltage then repair or replace as necessary
Ensure that the batteries are stored in a dust and damp free area
Check and ensure that battery terminations are secure, in good condition and appropriately greased
Apply a coating of Battery Terminal Grease or similar material to connectors and over the tops of cells
6 Monthly Maintenance Visit
All as per 3 monthly Maintenance Visits but with a check of 50% of the operation of the alarm devices in accordance with current regulations and manufacturers instructions
12 Monthly Maintenance Visit
Fire Alarm Systems
In addition to testing as for the three monthly maintenance Visits the following works should also be undertaken every year
100% test of all devices on the systems in accordance with the current regulations and manufacturers recommendations
Radio signal strengths in radio linked systems should be checked for adequacy
A visual inspection should be made to confirm that all readily accessible cable fixings are secured and undamaged
The cause and effect program should be confirmed as being correct
The standby power supply capacity should be checked to establish it remains suitable for continued service and replace if not
All further annual checks and tests recommended by the manufacturer of the control and indicating equipment and other components of the system should be carried out
Note: All testing products must be appropriate for purpose and the environment within which the systems are installed.
Test Certificates
All test certificates are to contain as a minimum
Relevant Aster UPRN
First line of address
Date of visit
System details
Clear indication of type of service
Time of Arrival and time of departure
Test results
Any defects rectified
Fire Fighting Equipment
General Information
The requirement is for the execution of a fully comprehensive planned servicing, testing, maintenance and responsive repairs service. The cost to provide this service will be included within the rates/prices within this pricing document to create the annual sum. The cost of any replacement equipment will be reimbursed at the rate included in this pricing document
Fire Fighting Equipment includes but is not limited to the following
Fire extinguishers (wet Chemical, CO2, Water, Foam and dry powder
Hose Reels
Fire Blankets
Progress meetings will be held quarterly. The contract administrator will chair the meeting and issue any minutes
Scope of Works
The contractor shall include within their annual testing, servicing and maintenance sum and is responsible for
Large parts and components (hoses, Horns & H Caps)
All consumables (O-rings, clips, pins etc…)
All discharge tests & refills as per BS5306
Wall fixings (where missing)
I D signs (where Missing)
Certificates of testing
Number all pieces of equipment and draw up a maintenance record sheet showing known service history
Providing information and reports should malicious damage be identified or suspected
Excluded from the contractors annual testing, servicing and maintenance sum
CO2 Hydraulic test
New equipment
Vandalism, malicious or mischievous damage/use of equipment
Misused/discharged equipment
Refilling of extinguishers due to discharge in the event of a fire
If the contract Administrator requires a replacement item of equipment, not included within the contractors responsibilities above, this will be subject to a separate Works Order. The cost of the replacement shall be determined by the rates contained within this pricing document.
The contractor shall note the priority coding will be in the majority - Routine Repairs
The contractor shall complete and supply the information with in an asset schedule report. The completed asset schedule report along with the properties serviced in the quarter, including the next service due date shall be attached to the contractors invoice. The contractor shall note that payment may be delayed if the information required is not fully supplied at the time of the invoice.
Maintenance Procedure
All equipment shall be maintained in accordance with current legislation
12 Monthly Maintenance Visits
Hand Held fire fighting equipment
Ensure all equipment is located correctly to suit risk
Ensure all equipment is correctly wall mounted and secure
Examine extinguisher body for cylinder damage
Inspect service history to determine service procedure
Inspect medium if required
Remove, check weight & date of cartridge
On stored pressure units, weigh full extinguisher and test head gauge
CO2 units check weight and cylinder date and ensure horn safe
Inspect all discharge paths and ensure they are clear and head assembly is fully operational
Examine all pressure seals and threads and ensure that they are not damaged. Lubricate as required
Ensure that retaining pin and anti-tamper tags are intact
Record service details
Five yearly visit
Hand held fire fighting equipment
On the fifth year of the extinguishers last discharge test, the contractor shall include for and carry out in addition to the above, a full discharge test and refill
All chemical discharge waste to be removed from site and appropriately disposed of. Certification of disposal process is required
Asset Schedule Report
The contractor shall assign a reference to every item of portable equipment on their initial maintenance visit. This information shall be logged in an asset schedule as approved by the contract administrator
Sprinkler Systems
General Information
The requirement is the execution of planned service, safety inspection and maintenance to the associations sprinkler systems
The requirement is a comprehensive contract including the execution of planned inspections testing, remedial works and emergency call out facility. The cost to provide these services will be included within the rates/prices provided in the pricing document for the annual sum per site. The cost of replacement components will be reimbursable.
The contractor shall note the priority coding of callouts will be in the majority Emergency Repairs
Quarterly progress meetings will be held
Scope of Works
Excluded from the contractors fully comprehensive cover are
Any repairs caused by storm, vandalism, flood or wilful neglect by third parties
Maintenance Procedure
The contractor shall carry out the inspection and testing of the system and equipment as recommended in TB203 the care and maintenance of automatic sprinkler systems
Dry Risers
General Information
The requirement is the execution of planned service, safety inspection and maintenance to dry Risers. The cost to provide this service will be included within the rates/prices contained within this document.
Progress meetings will be held quarterly
Scope of Work
The planned service, safety inspection and maintenance and repair will be undertaken by a competent person and to comply with the main requirements of BS9990:2015. The cost of replacement components will be at the rates and prices contained within the document.
Maintenance Procedure
6 Monthly Maintenance Visit
Inspection and if required repair of dry riser housing
Full visual inspection
Clear the riser of any debris
Check all exposed pipework and flanges
Check security of any anchor points and brackets
Check for integrity of fire stopping where pipes pass through walls or slab
Report Defects
Check condition of breaching connections and report
Check for full and free movement of all landing hydrant valves, checks hand wheel is secured correctly
Check all inlet and landing valves and associated washers are sound, replace as required
Check security of padlocks and tamper straps. Report back any issues
Check signage is correct and replace as necessary
12 Monthly Maintenance visit
Undertake a full test at pressure
Open the top valve of the system and flush out the system to remove any debris, ensuring no debris remains in the immediate vicinity
Test the system in accordance with current industry standards
Automatic Smoke Vents
General Information
The requirement is a fully comprehensive contract including the execution of planned inspections, testing, remedial works, and replacement components and emergency call out facility. The cost to provide these services will be included within the rates/prices provided in the pricing document for the annual sum
The contractor shall note the priority coding of call outs will be in the majority 'Emergency Repairs'
Scope of Works
Excluded from the contractors fully comprehensive cover are
Any repairs caused by storm, vandalism, flood or wilful neglect by third parties
Window glass and window frames unless the damage is caused by the contractor
Maintenance Procedure
The contractor shall carry out the inspection and testing of the systems and equipment as recommended in BS7346-8:2013 and BS558-5:2004. in particular the contractor must include for the following
6 monthly maintenance visits
Check and test that the smoke removal systems function correctly in fire conditions and close on resetting
Adjust and reset louvres, mechanisms and magnets as necessary to ensure smooth operation, leaving vent in fully working order
Repair and report any defects to contract administrator
Service all working parts
Record all results and service reports and issue to Contract Administrator within seven days of visit
General for all works Packages
Certificates
All works orders will be issued through Asters Contractor Portal. Training will be provided by Aster on its use. Orders will be issued though the portal, invoices submitted through the portal and all certificates necessitated for compliance and payment will be uploaded through the portal.

## Dayworks
Hourly Rates for Dayworks
Carried out on instruction from the contract Administrator only
Normal Working Hours | (Monday to Friday 8am to 8pm)
Fire Alarm Engineer |  | 0 | per hour
Electrical Engineer |  | 0 | per hour
General Builder |  | 0 | per hour
Electrician |  | 0 | per hour
Sprinkler system specialist |  | 0 | per hour
Dry Riser Engineer |  | 0 | per hour
Automatic Smoke Vent engineer |  | 0 | per hour
Outside Working Hours | Monday to Friday 8pm to 8am All day Saturday and Sunday- Bank Holidays)
Fire Alarm Engineer |  | 0 | per hour
Electrical Engineer |  | 0 | per hour
General Builder |  | 0 | per hour
Electrician |  | 0 | per hour
Sprinkler system specialist |  | 0 | per hour
Dry Riser Engineer |  | 0 | per hour
Automatic Smoke Vent engineer |  | 0 | per hour
Profit and Overheads on Dayworks items only
Profit on Materials |  |  | 0%
profit on plant, services, consumables and stores |  |  | 0%
profit on sub contractors |  |  | 0%
Site overheads |  |  | 0%
Overheads |  |  | 0%
Preliminaries |  |  | 0%

## Priorities
Priorities
It is anticipated that 90% of all works will be of a planned nature P3 and be undertaken within 14 days of order. This work will be a planned maintenance and servicing program
P1 | Emergency | Attend site and resolve within 2 hours of notification
P2 | Urgent | Attend site and resolve within 48 hours of notification
P3 | Routine | Attend site and resolve within 14 days of notification
Examples of priority (not exhaustive indicative only)
P1 | Report of sprinkler system failure/operation
P1 | Report of fire alarm fault
P2 | Damage to fire alarm call point
P2 | Report of fire extinguisher discharged
P3 | attend to carry out period/planned inspection

## Annual Variation
The Costs submitted within the schedule of rates and pricing document will be subject to an annual adjustment as from 1st April each year
The Price alteration will be based upon the 12month change percentage for the all items CPI indices from the ONS. The September indices will be applied on the adjustment date.
The first adjustment will be implemented in April 2020based upon the CPI for September 2019. And annually hereafter
Adjusted Prices will be applied to all works undertaken after 1st April each year.

## Collection Sheet
Fire Alarms | 0
Portable Fire Fighting Equipment | 0
Sprinkler Systems | 0
Dry Riser | 0
Automatic smoke Vents | 0
0