## ReadMe
Data as at	31/12/2022
Last updated	24/10/2024
Contact	enquiries@environment-agency.gov.uk

Tables
FLAAgglomerations	Details of non-compliant agglomerations
FLAUWWTPs	Details of non-compliant urban wastewater treatment plants

This report covers England only
For detailed descriptions of data fields, please see the FieldDescriptions tab

## FLAAgglomerations
flarepCode	aggCode	aggName	flaggStatus	flaggReasons	flaggMeasures	flaggExpecDateStart	flaggExpecDateStartWork	flaggExpecDateCompletion	flaggInv	flaggEUFundName	flaggEUFund	flaggComments	flaggExpLoad	flaggExpLoadColl	flaggExpLoadIAS	flaggOtherFund	flaggOtherFundName	flaggLoan	flaggLoanName
England	UKENTH_Agg000014	BECKTON	NC	Significant proportion of effluent not passing through full treatment instead discharging via storm overflows	Improved sewage treatment at the works both in terms of the volume that can be treated and the quality of the effluent. Over 55% expansion, new permit 4 years ago. Lee Tunnel construction to capture the flows that would previously have discharged to river from the Abbey Mills pumping station and conveying them to Beckton Sewage Treatment Works for full treatment. Tideway Tunnel construction to capture the flows that would previously have discharged to river and conveying them to Beckton Sewage Treatment Works for full treatment. The Tideway and Lee Tunnel were connected in May 2024. The London Tideway Tunnels, (the combined Lee Tunnel and Thames Tideway Tunnel), is now live and able to accept storm flows from Abbey Mills Pumping Station. / The Tideway Tunnel is currently undergoing System Activation where each of the new sewer interception sites are connected to the tunnel to reduce spills to the tidal River Thames. Four sites have already been activated. / Further sites will be activated in the coming weeks. Tideway are aiming to complete activation at all their sites by December 2024 when System Commissioning will begin. / Commissioning will ensure that the entire system works effectively under various storm conditions , before the London Tideway Tunnels become fully operational in 2025.	2006-12-01	2010-04-01	2023-07-01	5763.72	na	0	Investment figures in £ sterling	2920685	100	0
England	UKENTH_Agg000052	CROSSNESS	NC	Significant proportion of effluent not passing through full treatment instead discharging via storm overflows	Improved sewage treatment at the works both in terms of the volume that can be treated and the quality of the effluent. Expanded by 46%, new permit 4 years ago. Tideway Tunnel construction to capture the flows that would previously have discharged to river and conveying them to Crossness Sewage Treatment Works for full treatment. See note above on progress with the tunnel.	2006-12-01	2010-08-01	2023-07-01	5069.91	na	0	Investment figures in £ sterling	1604197	100	0
England	UKENNE_Agg000028	HENDON	NC	The frequency of discharge via storm overflows is considered too large.	The works were completed in December 2017 with spill data reported to the Commission every 6 months. Monitoring will continue until there is 10 years data. It will be subject to further improvement work to reduce spills in line with the Governments Storm Overflow Reduction Plan in due course.	2013-04-01	2016-11-01	2017-12-01	7.08	na	0	Investment figures in £ sterling	197491	100	0

## FLAUWWTPs
flarepCode	uwwCode	uwwName	flatpStatus	flatpReasons	flatpMeasures	flatpExpLoad	flatpExpCapacity	flatpExpecTreatment	flatpExpecDateStart	flatpExpecDateStartWork	flatpExpecDateCompletion	flatpExpecDatePerformance	flatpInv	flatpEUFundName	flatpEUFund	flatpComments	flatpExpLoadTruck	flatpOtherFund	flatpOtherFundName	flatpLoan	flatpLoanName
England	UKENAN_AW_TP000016	BEDFORD STW F/E	NC	Annual effluent mean and annual mean % reduction fail for P	No correspondence with the company regarding these failures and there are no active investigations. / They become compliant in 2023.	187553	197000	3P				01/01/2023
England	UKENAN_AW_TP000115	CAISTER STW F/E	NC	Non-compliant UWWTD sample - Upper Tier COD failure. Non-compliant UWWTD sample - Upper Tier BOD failure.	Failures were due to an issue with the blowers providing the dissolved oxygen for the activated sludge lane and the returned activated sludge bell mouths were also running in manual fixed positions. There were then elevated flows due to a rain event that led to partially treated effluent being discharged. This event was quickly resolved once flows dropped to normal. Company quickly replaced the defective blower. They also exchanged one of the larger blowers for two smaller blowers to give more resilience. No enforcement by EA. One failure since in 2024 for different reasons.	108313	170000	2				01/01/2023
England	UKENAN_AW_TP000056	CLACTON STW F/E	NC	Non-compliant UWWTD sample - Upper Tier COD failure.	Company investigated and made repairs including to a flow to treatment control valve. There have been no further breaches. We issued the company with a warning letter for the breach of permit.	46344	54838	2				01/01/2023
England	UKENAN_AW_TP000143	INGOLDMELLS STW F/E	NC	Non-compliant UWWTD sample - Upper Tier COD failure. Non-compliant UWWTD sample - Upper Tier BOD failure.	Similar issues in 2022 as in 2020. Company have provided measures they have been putting in place to ensure future compliance. No failures since 2022. Case file for both breaches is with EA Legal	45387	100000	2				01/01/2023
England	UKENAN_AW_TP000267	TOWCESTER STW F/E	NC	Annual effluent mean and annual mean % reduction fail for N	No correspondence with the company regarding these failures and there are no active investigations. / They become compliant in 2023.	12337	12337	3N				01/01/2023
England	UKENAN_AW_TP000286	WHILTON (Daventry) STW F/E	NC	Insufficient phosphate samples	The company's lab’s computer system replacement resulted in scheduling issues, and we are still investigating. It looks like the issue was confined to 2022	32506	47800	3P				01/01/2023
England	UKENNW_UU_TP000110	SANDON DOCK WWTW FINAL EFF OUTLET 1&2	NC	Non-compliant UWWTD sample - Upper Tier BOD failure.	Company was managing failure of one of the digesters due to a failing in the mixer pipework. This necessitated the exporting of all sludge via tankers to alternative sites. Compliance was maintained until the day of failure, when there was a sharp and unexplained flow increase during a dry period. Company conducted an investigation into potential source of the unexplained increase in flow. EA issued a Warning Letter.	664250	693484	2				01/01/2023
England	UKENSO_ALB_TP001	NORTHFLEET EASTERN QUARRY WWTW	NC	No samples	EA writing compliance notices to obtain PE figure and general plan to meet UWWTD regulations. We have had various site visits and other correspondence offering advice and guidance but this has not achieved the desired effect.	4000		2				01/01/2025
England	UKENSO_SW_TP000100	PAGHAM STW	NC	Potential Eutrophic N fail (indirect - Pagham Harbour)	This agglomeration recently crossed the 10000 threshold for population equivalent and N removal is yet to be implemented. This will form part of the planning for PR24 (2025 to 2030) investment period by the water companies with the improvements implemented post 2025	12424		3N			31/12/2030	31/12/2030
England	UKENMI_ST_TP000051	CHEDDLETON STW	NC	Potential Eutrophic P fail (indirect)	Plans are already in place for this treatment plant to have sufficient P removal in place to meet the UWWTR P limit by the end of AMP7 (2030). A permit update is required.	10072		3P			31/12/2030	31/12/2030
England	UKENMI_ST_TP000229	WESTWOOD BROOK STW	NC	Potential Eutrophic P fail (indirect)	Plans are already in place for this treatment plant to have sufficient P removal in place to meet the UWWTR P limit by the end of 2026 as part of the Green Recovery Project. A permit update is required.	10010		3P			31/12/2026	31/12/2026
England	UKENMI_ST_TP000005	ALVECHURCH SEWAGE TREATMENT WORKS	NC	Potential Eutrophic P fail (direct)	Plans are already in place for this treatment plant to have sufficient P removal in place to meet the UWWTR P limit by the end of AMP7 (2030). A permit update is required.	10115		3P			31/12/2030	31/12/2030
England	UKENMI_ST_TP000019	BARROW & QUORN STW	NC	Potential Eutrophic P fail (indirect)	P removal began March 2022	12835		3P				01/01/2023
England	UKENNW_UU_TP000010	AUDLEY WASTEWATER TREATMENT WORKS	NC	Potential Eutrophic P fail (indirect)	The population equivalent for Audley dropped below the 10 000 PE threshold in 2023 and therefore no nutrient removal is currently planned.	10065		3P				01/01/2023
England	UKENTH_TWU_TP000042	CHIPPING NORTON WWTW	NC	Potential Eutrophic P fail (indirect)	Plans are already in place for this treatment plant to have sufficient P removal in place to meet the UWWTR P limit by 13/05/2030.	10552		3P			13/05/2030	13/05/2030
England	UKENTH_TWU_TP000030	BURSTOW WASTEWATER TREATMENT WORKS	NC	Potential Eutrophic P fail (indirect)	P removal began November 2022	11696		3P				01/01/2023
England	UKENTH_TWU_TP000109	MERSTHAM WWTW	NC	Potential Eutrophic P fail (indirect)	Plans are already in place for this treatment plant to have sufficient P removal in place to meet the UWWTR P limit by 13/05/2030.	10098		3P			13/05/2030	13/05/2030
England	UKENNW_UU_TP000001	AINSDALE WASTEWATER TREATMENT WORKS	NC	Potential Eutrophic P fail (indirect)	A scheme is in place for Ainsdale WwTW to achieve P removal by 31/03/2025	10260		3P			31/03/2025	31/03/2025
England	UKENAN_AW_TP000008	AYLSHAM STW	NC	Potential Eutrophic P fail (indirect)	UWWTR P monitoring due to be in place by 31 March 2025.	10229		3P			31/03/2025	31/03/2025

## FieldDescriptions
FLAAgglomerations				FLAUWWTPs				Treatment codes
								Code	Label
Field	Description			Field	Description			1	primary treatment
flarepCode	Reporting Area			flarepCode	Reporting Area			2	secondary treatment
aggCode	Agglomeration Code - Unique identifier for agglomeration			uwwCode	Urban waste water treatment plant code - Unique identifier for treatment plant			3m	more stringent disinfection
aggName	Agglomeration Name			uwwName	Urban waste water treatment plant name			3N	more stringent nitrogen removal
flaggStatus	Agglomeration Status (C = compliant;NC = Non-compliant)			flatpStatus	Treatment plant status (C = compliant; NC = Non-compliant)			3Nm	more stringent nitrogen removal and disinfection
flaggReasons	Reason for non-compliance			flatpReasons	Reason for non-compliance			3NP	more stringent nitrogen and phosphorus
flaggMeasures	Measures being taken to address non-compliance			flatpMeasures	Measures being taken to address non-compliance			3NPm	more stringent nitrogen and phosphorus removal and disinfection
flaggExpecDateStart	Expected data for preparatory work to start			flatpExpLoad	Expected load (PE) of treatment plant			3other	any other more stringent treatment
flaggExpecDateStartWork	Expected date for work to start			flatpExpCapacity	Expected capacity (PE) of treatment plant			3P	more stringent phosphorus removal
flaggExpecDateCompletion	Expected date for work to be completed			flatpExpecTreatment	Expected treatment - see treatment codes table			3Pm	more stringent phosphorus removal and disinfection
flaggInv	Investment (pounds sterling)			flatpExpecDateStart	Expected data for preparatory work to start
flaggEUFundName	N/A			flatpExpecDateStartWork	Expected date for work to start
flaggEUFund	N/A			flatpExpecDateCompletion	Expected date for work to be completed
flaggComments	Comments			flatpExpecDatePerformance	Expected that of compliance
flaggExpLoad	Expected load (PE) of agglomeration			flatpInv	Investment (pounds sterling)
flaggExpLoadColl	Expected load collected			flatpEUFundName	N/A
flaggExpLoadIAS	Expected load dealt with via Individual Appropriate Systems (IAS)			flatpEUFund	N/A
flaggOtherFund	N/A			flatpComments
flaggOtherFundName	N/A			flatpExpLoadTruck	N/A
flaggLoan	N/A			flatpOtherFund	N/A
				flatpOtherFundName	N/A
				flatpLoan	N/A
				flatpLoanName	N/A